ModBus protocol address table-DTSU666

| Parameter address | Parameter code | Instructions of parameters | Data type | Data length Word | Read Write |
| --- | --- | --- | --- | --- | --- |
| Keyboard parameters (specific parameters see the instructions of programming parameters, the actual value with (*) parameter＝ communication parameter value × 0.1） |  |  |  |  |  |
| 0000H | REV. | Software Version | Signed | 1 | R |
| 0001H | UCode | Programming code codE(1～9999) | Signed | 1 | R/W |
| 0003H | net | Network selection (0:three phase four wire, 1:three phase three wire) | Signed | 1 | R/W |
| 0006H | IrAt | Current transformer rate IrAt(1～9999) | Signed | 1 | R/W |
| 0007H | UrAt | Voltage transformer rate UrAt（*） (1～9999 represents voltage ratio 0.1～999.9) | Signed | 1 | R/W |
| 000AH | Disp | Rotating display time（0-30s，0：no rotating） | Signed | 1 | R/W |
| 000BH | B.LCD | Backlight time control（0-30min，0：always on） | Signed | 1 | R/W |
| 002BH | UUID | Device type ID(0～9999) | bit | 1 | R |
| 002CH | Protocol | Protocol switching [0:Modbus;1:DL/T645] | Signed | 1 | R/W |
| 002DH | bAud | [0:1200;1:2400;2:4800;3:9600; 4;19200;5:38400;6:115200] | Signed | 1 | R/W |
| 002EH | Addr | Communication address Addr(1～247) | Signed | 1 | R/W |
| 0035H | SN1 | Last 4 number of SN | BCD | 1 | R |
| 0036H | SN2 | Middle 4 number of SN | BCD | 1 | R |
| 0037H | SN3 | First 4 number of SN | BCD | 1 | R |
| 0045H | CID | Customer ID(0～9999) | Signed | 1 | R |
| Electricity data on the secondary side-1st circuit |  |  |  |  |  |
| 0200H | Uab | Three phase line voltage data, Unit V(×0.1V) | float | 2 | R |
| 0202H | Ubc |  | float | 2 | R |
| 0204H | Uca |  | float | 2 | R |
| 0206H | Ua | Three phase voltage data, Unit V(×0.1V) (Invalid for three phase three wire) | float | 2 | R |
| 0208H | Ub |  | float | 2 | R |
| 020AH | Uc |  | float | 2 | R |
| 020CH | Ia | Three phase current data, Unit A(×0.001A) | float | 2 | R |
| 020EH | Ib |  | float | 2 | R |
| 0210H | Ic |  | float | 2 | R |
| 0212H | Pt | Combined active power, Unit W(×0.1W) | float | 2 | R |
| 0214H | Pa | A phase active power, Unit W(×0.1W) | float | 2 | R |
| 0216H | Pb | B phase active power, Unit W(×0.1W) (Invalid for three phase three wire) | float | 2 | R |
| 0218H | Pc | C phase active power, Unit W(×0.1W) | float | 2 | R |
| 021AH | Qt | Combined reactive power, Unit var(×0.1var) | float | 2 | R |
| 021CH | Qa | A phase reactive power, Unit var(×0.1var) | float | 2 | R |
| 021EH | Qb | B phase reactive power, Unit var(×0.1var) (Invalid for three phase three wire) | float | 2 | R |
| 0220H | Qc | C phase reactive power, Unit var(×0.1var) | float | 2 | R |
| 022AH | PFt | Combined power factor(forward number：inductive，reverse number：capacitive) (×0.001) | float | 2 | R |
| 022CH | PFa | A phase power factor(forward number：inductive，reverse number：capacitive) (Invalid for three phase three wire) (×0.001) | float | 2 | R |
| 022EH | PFb | B phase power factor(forward number：inductive，reverse number：capacitive) (Invalid for three phase three wire) (×0.001) | float | 2 | R |
| 0230H | PFc | C phase power factor(forward number：inductive，reverse number：capacitive) (Invalid for three phase three wire) (×0.001) | float | 2 | R |
| 0244H | Freq | Frequency, Unit Hz(×0.01Hz) | float | 2 | R |
| energy secondary side data-1st circuit |  |  |  |  |  |
| 0100H | EpCom | （current）Total combination active energy(kWh) | float | 2 | R |
| 010AH | EqCom1 | （current）Total combination reactive energy 1(kvarh) | float | 2 | R |
| 0114H | EqCom2 | （current）Total combination reactive energy 2(kvarh) | float | 2 | R |
| 011EH | ImpEp | （current）Total Forward active energy(kWh) | float | 2 | R |
| 0120H | ImpEpA | （current）A Forward active energy(kWh) | float | 2 | R |
| 0122H | ImpEpB | （current）B Forward active energy(kWh) | float | 2 | R |
| 0124H | ImpEpC | （current）C Forward active energy(kWh) | float | 2 | R |
| 0126H | NetImpEp | （current）Net Forward active energy(kWh) | float | 2 | R |
| 0128H | ExpEp | （current）Total Reverse active energy(kWh) | float | 2 | R |
| 012AH | ExpEpA | （current）A Reverse active energy(kWh) | float | 2 | R |
| 012CH | ExpEpB | （current）B Reverse active energy(kWh) | float | 2 | R |
| 012EH | ExpEpC | （current）C Reverse active energy(kWh) | float | 2 | R |
| 0130H | NetExpEp | （current）Net Reverse active energy(kWh) | float | 2 | R |
| Electricity data on the secondary side-2nd circuit |  |  |  |  |  |
| 0900H | Uab | Three phase line voltage data, Unit V(×0.1V) | float | 2 | R |
| 0902H | Ubc |  | float | 2 | R |
| 0904H | Uca |  | float | 2 | R |
| 0906H | Ua | Three phase voltage data, Unit V(×0.1V) (Invalid for three phase three wire) | float | 2 | R |
| 0908H | Ub |  | float | 2 | R |
| 090AH | Uc |  | float | 2 | R |
| 090CH | Ia | Three phase current data, Unit A(×0.001A) | float | 2 | R |
| 090EH | Ib |  | float | 2 | R |
| 0910H | Ic |  | float | 2 | R |
| 0912H | Pt | Combined active power, Unit W(×0.1W) | float | 2 | R |
| 0914H | Pa | A phase active power, Unit W(×0.1W) | float | 2 | R |
| 0916H | Pb | B phase active power, Unit W(×0.1W) (Invalid for three phase three wire) | float | 2 | R |
| 0918H | Pc | C phase active power, Unit W(×0.1W) | float | 2 | R |
| 091AH | Qt | Combined reactive power, Unit var(×0.1var) | float | 2 | R |
| 091CH | Qa | A phase reactive power, Unit var(×0.1var) | float | 2 | R |
| 091EH | Qb | B phase reactive power, Unit var(×0.1var) (Invalid for three phase three wire) | float | 2 | R |
| 0920H | Qc | C phase reactive power, Unit var(×0.1var) | float | 2 | R |
| 092AH | PFt | Combined power factor(forward number：inductive，reverse number：capacitive) (×0.001) | float | 2 | R |
| 092CH | PFa | A phase power factor(forward number：inductive，reverse number：capacitive) (Invalid for three phase three wire) (×0.001) | float | 2 | R |
| 092EH | PFb | B phase power factor(forward number：inductive，reverse number：capacitive) (Invalid for three phase three wire) (×0.001) | float | 2 | R |
| 0930H | PFc | C phase power factor(forward number：inductive，reverse number：capacitive) (Invalid for three phase three wire) (×0.001) | float | 2 | R |
| 0944H | Freq | Frequency, Unit Hz(×0.01Hz) | float | 2 | R |
| energy secondary side data-2nd circuit |  |  |  |  |  |
| 0800H | EpCom | （current）Total combination active energy(kWh) | float | 2 | R |
| 080AH | EqCom1 | （current）Total combination reactive energy 1(kvarh) | float | 2 | R |
| 0814H | EqCom2 | （current）Total combination reactive energy 2(kvarh) | float | 2 | R |
| 081EH | ImpEp | （current）Total Forward active energy(kWh) | float | 2 | R |
| 0820H | ImpEpA | （current）A Forward active energy(kWh) | float | 2 | R |
| 0822H | ImpEpB | （current）B Forward active energy(kWh) | float | 2 | R |
| 0824H | ImpEpC | （current）C Forward active energy(kWh) | float | 2 | R |
| 0826H | NetImpEp | （current）Net Forward active energy(kWh) | float | 2 | R |
| 0828H | ExpEp | （current）Total Reverse active energy(kWh) | float | 2 | R |
| 082AH | ExpEpA | （current）A Reverse active energy(kWh) | float | 2 | R |
| 082CH | ExpEpB | （current）B Reverse active energy(kWh) | float | 2 | R |
| 082EH | ExpEpC | （current）C Reverse active energy(kWh) | float | 2 | R |
| 0830H | NetExpEp | （current）Net Reverse active energy(kWh) | float | 2 | R |